## Test Execution
Test ID | Test / Objective | Step | Input / Test Condition | Input Value | Input Unit | Expected DUT Value | DUT Unit | Min Accepted | Max Accepted | Actual Measured | Result | Acceptance / Notes
AI-01 | 4-20 mA channel accuracy and linearity for TC1 | 1 | Inject 4 mA to TC1, TC2 and CC individually; repeat with all three channels active. | 4 | mA | 0 | A | -0.25 | 0.25 | 0 | PASS | TC1/TC2/CC instantaneous values correspond to configured scaling within +/-0.5% FS. No material crosstalk when channels are driven simultaneously. | 50
AI-01 | 4-20 mA channel accuracy and linearity for TC1 | 2 | Inject 8 mA to TC1, TC2 and CC individually; repeat with all three channels active. | 8 | mA | 12.5 | A | 12.25 | 12.75 | 12.38 | PASS | TC1/TC2/CC instantaneous values correspond to configured scaling within +/-0.5% FS. No material crosstalk when channels are driven simultaneously.
AI-01 | 4-20 mA channel accuracy and linearity for TC1 | 3 | Inject 12 mA to TC1, TC2 and CC individually; repeat with all three channels active. | 12 | mA | 25 | A | 24.75 | 25.25 | 24.82 | PASS | TC1/TC2/CC instantaneous values correspond to configured scaling within +/-0.5% FS. No material crosstalk when channels are driven simultaneously.
AI-01 | 4-20 mA channel accuracy and linearity for TC1 | 4 | Inject 16 mA to TC1, TC2 and CC individually; repeat with all three channels active. | 16 | mA | 37.5 | A | 37.25 | 37.75 | 37.26 | PASS | TC1/TC2/CC instantaneous values correspond to configured scaling within +/-0.5% FS. No material crosstalk when channels are driven simultaneously.
AI-01 | 4-20 mA channel accuracy and linearity for TC1 | 5 | Inject 20 mA to TC1, TC2 and CC individually; repeat with all three channels active. | 20 | mA | 50 | A | 49.75 | 50.25 | 49.7 | FAIL | TC1/TC2/CC instantaneous values correspond to configured scaling within +/-0.5% FS. No material crosstalk when channels are driven simultaneously.
AI-01 | 4-20 mA channel accuracy and linearity for TC2 | 1 | Inject 4 mA to TC1, TC2 and CC individually; repeat with all three channels active. | 4 | mA | 0 | A | -0.25 | 0.25 | 0 | PASS | TC1/TC2/CC instantaneous values correspond to configured scaling within +/-0.5% FS. No material crosstalk when channels are driven simultaneously.
AI-01 | 4-20 mA channel accuracy and linearity for TC2 | 2 | Inject 8 mA to TC1, TC2 and CC individually; repeat with all three channels active. | 8 | mA | 12.5 | A | 12.25 | 12.75 | 12.37 | PASS | TC1/TC2/CC instantaneous values correspond to configured scaling within +/-0.5% FS. No material crosstalk when channels are driven simultaneously.
AI-01 | 4-20 mA channel accuracy and linearity for TC2 | 3 | Inject 12 mA to TC1, TC2 and CC individually; repeat with all three channels active. | 12 | mA | 25 | A | 24.75 | 25.25 | 24.81 | PASS | TC1/TC2/CC instantaneous values correspond to configured scaling within +/-0.5% FS. No material crosstalk when channels are driven simultaneously.
AI-01 | 4-20 mA channel accuracy and linearity for TC2 | 4 | Inject 16 mA to TC1, TC2 and CC individually; repeat with all three channels active. | 16 | mA | 37.5 | A | 37.25 | 37.75 | 37.25 | PASS | TC1/TC2/CC instantaneous values correspond to configured scaling within +/-0.5% FS. No material crosstalk when channels are driven simultaneously.
AI-01 | 4-20 mA channel accuracy and linearity for TC2 | 5 | Inject 20 mA to TC1, TC2 and CC individually; repeat with all three channels active. | 20 | mA | 50 | A | 49.75 | 50.25 | 49.68 | FAIL | TC1/TC2/CC instantaneous values correspond to configured scaling within +/-0.5% FS. No material crosstalk when channels are driven simultaneously.
AI-01 | 4-20 mA channel accuracy and linearity for CC | 1 | Inject 4 mA to TC1, TC2 and CC individually; repeat with all three channels active. | 4 | mA | 0 | A | -0.25 | 0.25 | 0 | PASS | TC1/TC2/CC instantaneous values correspond to configured scaling within +/-0.5% FS. No material crosstalk when channels are driven simultaneously.
AI-01 | 4-20 mA channel accuracy and linearity for CC | 2 | Inject 8 mA to TC1, TC2 and CC individually; repeat with all three channels active. | 8 | mA | 12.5 | A | 12.25 | 12.75 | 12.38 | PASS | TC1/TC2/CC instantaneous values correspond to configured scaling within +/-0.5% FS. No material crosstalk when channels are driven simultaneously.
AI-01 | 4-20 mA channel accuracy and linearity for CC | 3 | Inject 12 mA to TC1, TC2 and CC individually; repeat with all three channels active. | 12 | mA | 25 | A | 24.75 | 25.25 | 24.81 | PASS | TC1/TC2/CC instantaneous values correspond to configured scaling within +/-0.5% FS. No material crosstalk when channels are driven simultaneously.
AI-01 | 4-20 mA channel accuracy and linearity for CC | 4 | Inject 16 mA to TC1, TC2 and CC individually; repeat with all three channels active. | 16 | mA | 37.5 | A | 37.25 | 37.75 | 37.25 | PASS | TC1/TC2/CC instantaneous values correspond to configured scaling within +/-0.5% FS. No material crosstalk when channels are driven simultaneously.
AI-01 | 4-20 mA channel accuracy and linearity for CC | 5 | Inject 20 mA to TC1, TC2 and CC individually; repeat with all three channels active. | 20 | mA | 50 | A | 49.75 | 50.25 | 49.69 | FAIL | TC1/TC2/CC instantaneous values correspond to configured scaling within +/-0.5% FS. No material crosstalk when channels are driven simultaneously.
AI-02 | Motor input accuracy for 4-20 mA and/or 0-333 mV configuration. | 1 | Configure motor input for 4-20 mA; apply 0% FS. | 4 | mA | 0 | A | -1 | 1 | 0 | PASS | Within +/-1% FS for motor instantaneous measurement. Unsupported mode is documented rather than assumed.
AI-02 | Motor input accuracy for 4-20 mA and/or 0-333 mV configuration. | 2 | Configure motor input for 4-20 mA; apply 25% FS. | 8 | mA | 25 | A | 24 | 26 | 24.75 | PASS | Within +/-1% FS for motor instantaneous measurement. Unsupported mode is documented rather than assumed.
AI-02 | Motor input accuracy for 4-20 mA and/or 0-333 mV configuration. | 3 | Configure motor input for 4-20 mA; apply 50% FS. | 12 | mA | 50 | A | 49 | 51 | 49.62 | PASS | Within +/-1% FS for motor instantaneous measurement. Unsupported mode is documented rather than assumed.
AI-02 | Motor input accuracy for 4-20 mA and/or 0-333 mV configuration. | 4 | Configure motor input for 4-20 mA; apply 75% FS. | 16 | mA | 75 | A | 74 | 76 | 74.5 | PASS | Within +/-1% FS for motor instantaneous measurement. Unsupported mode is documented rather than assumed.
AI-02 | Motor input accuracy for 4-20 mA and/or 0-333 mV configuration. | 5 | Configure motor input for 4-20 mA; apply 100% FS. | 20 | mA | 100 | A | 99 | 101 | 99.38 | PASS | Within +/-1% FS for motor instantaneous measurement. Unsupported mode is documented rather than assumed.
AI-02 | Motor input accuracy for 4-20 mA and/or 0-333 mV configuration. | 6 | Configure motor input for 0-333 mV; apply 0% FS. | 0 | mV | 0 | A | -1 | 1 | 0.007 | PASS | Within +/-1% FS for motor instantaneous measurement. Unsupported mode is documented rather than assumed.
AI-02 | Motor input accuracy for 4-20 mA and/or 0-333 mV configuration. | 7 | Configure motor input for 0-333 mV; apply 25% FS. | 83.25 | mV | 25 | A | 24 | 26 | 24.98 | PASS | Within +/-1% FS for motor instantaneous measurement. Unsupported mode is documented rather than assumed.
AI-02 | Motor input accuracy for 4-20 mA and/or 0-333 mV configuration. | 8 | Configure motor input for 0-333 mV; apply 50% FS. | 166.5 | mV | 50 | A | 49 | 51 | 49.97 | PASS | Within +/-1% FS for motor instantaneous measurement. Unsupported mode is documented rather than assumed.
AI-02 | Motor input accuracy for 4-20 mA and/or 0-333 mV configuration. | 9 | Configure motor input for 0-333 mV; apply 75% FS. | 249.75 | mV | 75 | A | 74 | 76 | 74.97 | PASS | Within +/-1% FS for motor instantaneous measurement. Unsupported mode is documented rather than assumed.
AI-02 | Motor input accuracy for 4-20 mA and/or 0-333 mV configuration. | 10 | Configure motor input for 0-333 mV; apply 100% FS. | 333 | mV | 100 | A | 99 | 101 | 99.97 | PASS | Within +/-1% FS for motor instantaneous measurement. Unsupported mode is documented rather than assumed.
AI-03 | Load-current 0-333 mV accuracy. | 1 | Apply 50 Hz sinusoidal load-current signal at 10% FS. | 33.3 | mV RMS | 2 | A RMS | 1.8 | 2.2 | 1.998 | PASS | Instantaneous/RMS values satisfy applicable requirements; scaling is stable at both 50 and 60 Hz.
AI-03 | Load-current 0-333 mV accuracy. | 2 | Apply 50 Hz sinusoidal load-current signal at 25% FS. | 83.25 | mV RMS | 5 | A RMS | 4.8 | 5.2 | 4.996 | PASS | Instantaneous/RMS values satisfy applicable requirements; scaling is stable at both 50 and 60 Hz.
AI-03 | Load-current 0-333 mV accuracy. | 3 | Apply 50 Hz sinusoidal load-current signal at 50% FS. | 166.5 | mV RMS | 10 | A RMS | 9.8 | 10.2 | 9.994 | PASS | Instantaneous/RMS values satisfy applicable requirements; scaling is stable at both 50 and 60 Hz.
AI-03 | Load-current 0-333 mV accuracy. | 4 | Apply 50 Hz sinusoidal load-current signal at 75% FS. | 249.75 | mV RMS | 15 | A RMS | 14.8 | 15.2 | 14.99 | PASS | Instantaneous/RMS values satisfy applicable requirements; scaling is stable at both 50 and 60 Hz.
AI-03 | Load-current 0-333 mV accuracy. | 5 | Apply 50 Hz sinusoidal load-current signal at 100% FS. | 333 | mV RMS | 20 | A RMS | 19.8 | 20.2 | 19.99 | PASS | Instantaneous/RMS values satisfy applicable requirements; scaling is stable at both 50 and 60 Hz.
AI-03 | Load-current 0-333 mV accuracy. | 6 | Apply 60 Hz sinusoidal load-current signal at 10% FS. | 33.3 | mV RMS | 2 | A RMS | 1.8 | 2.2 | 1.998 | PASS | Instantaneous/RMS values satisfy applicable requirements; scaling is stable at both 50 and 60 Hz.
AI-03 | Load-current 0-333 mV accuracy. | 7 | Apply 60 Hz sinusoidal load-current signal at 25% FS. | 83.25 | mV RMS | 5 | A RMS | 4.8 | 5.2 | 4.993 | PASS | Instantaneous/RMS values satisfy applicable requirements; scaling is stable at both 50 and 60 Hz.
AI-03 | Load-current 0-333 mV accuracy. | 8 | Apply 60 Hz sinusoidal load-current signal at 50% FS. | 166.5 | mV RMS | 10 | A RMS | 9.8 | 10.2 | 9.997 | PASS | Instantaneous/RMS values satisfy applicable requirements; scaling is stable at both 50 and 60 Hz.
AI-03 | Load-current 0-333 mV accuracy. | 9 | Apply 60 Hz sinusoidal load-current signal at 75% FS. | 249.75 | mV RMS | 15 | A RMS | 14.8 | 15.2 | 15 | PASS | Instantaneous/RMS values satisfy applicable requirements; scaling is stable at both 50 and 60 Hz.
AI-03 | Load-current 0-333 mV accuracy. | 10 | Apply 60 Hz sinusoidal load-current signal at 100% FS. | 333 | mV RMS | 20 | A RMS | 19.8 | 20.2 | 20 | PASS | Instantaneous/RMS values satisfy applicable requirements; scaling is stable at both 50 and 60 Hz.
AV-01 | DC voltage accuracy from 0 to 150 VDC. | 1 | Apply isolated 0 VDC to control-voltage input. | 0 | VDC | 0 | VDC | -0.75 | 0.75 | 0.015 | PASS | Measured control voltage is within +/-0.5% FS at all points.
AV-01 | DC voltage accuracy from 0 to 150 VDC. | 2 | Apply isolated 15 VDC to control-voltage input. | 15 | VDC | 15 | VDC | 14.25 | 15.75 | 15.04 | PASS | Measured control voltage is within +/-0.5% FS at all points.
AV-01 | DC voltage accuracy from 0 to 150 VDC. | 3 | Apply isolated 37.5 VDC to control-voltage input. | 37.5 | VDC | 37.5 | VDC | 36.75 | 38.25 | 37.54 | PASS | Measured control voltage is within +/-0.5% FS at all points.
AV-01 | DC voltage accuracy from 0 to 150 VDC. | 4 | Apply isolated 75 VDC to control-voltage input. | 75 | VDC | 75 | VDC | 74.25 | 75.75 | 75.08 | PASS | Measured control voltage is within +/-0.5% FS at all points.
AV-01 | DC voltage accuracy from 0 to 150 VDC. | 5 | Apply isolated 112.5 VDC to control-voltage input. | 112.5 | VDC | 112.5 | VDC | 111.75 | 113.25 | 112.62 | PASS | Measured control voltage is within +/-0.5% FS at all points.
AV-01 | DC voltage accuracy from 0 to 150 VDC. | 6 | Apply isolated 150 VDC to control-voltage input. | 150 | VDC | 150 | VDC | 149.25 | 150.75 | 150.51 | PASS | Measured control voltage is within +/-0.5% FS at all points.
AV-02 | AC voltage accuracy at 50 and 60 Hz. | 1 | Apply 15 VAC at 50 Hz. | 15 | VAC RMS | 15 | VAC RMS | 14.25 | 15.75 | 14.99 | PASS | Measured value is within +/-0.5% FS where the firmware reports AC RMS. No unintended channel mode change.
AV-02 | AC voltage accuracy at 50 and 60 Hz. | 2 | Apply 75 VAC at 50 Hz. | 75 | VAC RMS | 75 | VAC RMS | 74.25 | 75.75 | 75.31 | PASS | Measured value is within +/-0.5% FS where the firmware reports AC RMS. No unintended channel mode change.
AV-02 | AC voltage accuracy at 50 and 60 Hz. | 3 | Apply 150 VAC at 50 Hz. | 150 | VAC RMS | 150 | VAC RMS | 149.25 | 150.75 | 150.62 | PASS | Measured value is within +/-0.5% FS where the firmware reports AC RMS. No unintended channel mode change.
AV-02 | AC voltage accuracy at 50 and 60 Hz. | 4 | Apply 15 VAC at 60 Hz. | 15 | VAC RMS | 15 | VAC RMS | 14.25 | 15.75 |  |  | Measured value is within +/-0.5% FS where the firmware reports AC RMS. No unintended channel mode change.
AV-02 | AC voltage accuracy at 50 and 60 Hz. | 5 | Apply 75 VAC at 60 Hz. | 75 | VAC RMS | 75 | VAC RMS | 74.25 | 75.75 |  |  | Measured value is within +/-0.5% FS where the firmware reports AC RMS. No unintended channel mode change.
AV-02 | AC voltage accuracy at 50 and 60 Hz. | 6 | Apply 150 VAC at 60 Hz. | 150 | VAC RMS | 150 | VAC RMS | 149.25 | 150.75 |  |  | Measured value is within +/-0.5% FS where the firmware reports AC RMS. No unintended channel mode change.
PWR-01 | Nominal supply operation at 24 VDC. | 1 | Apply DUT supply at 24.0 VDC and execute baseline acquisition/communications. | 24 | VDC | Functional operation |  | N/A | N/A |  |  | Normal startup and operation; no reset or fault; values recorded as baseline.
PWR-02 | Specified lower limit 21.6 VDC. | 1 | Apply DUT supply at 21.6 VDC and execute baseline acquisition/communications. | 21.6 | VDC | Functional operation |  | N/A | N/A |  |  | No reboot, data corruption or acquisition error. All active measurements remain within specified accuracy.
PWR-03 | Specified upper limit 26.4 VDC. | 1 | Apply DUT supply at 26.4 VDC and execute baseline acquisition/communications. | 26.4 | VDC | Functional operation |  | N/A | N/A |  |  | No abnormal heating, reboot, measurement shift beyond tolerance or error log unrelated to test.
DI-03 | Representative field-voltage operation. | 1 | Apply 24 VDC to applicable DI threshold variant and toggle 100 times. | 24 | VDC | Correct ON/OFF state |  | N/A | N/A |  |  | Correct state is reported for every operation; no missed/extra transitions.
DI-03 | Representative field-voltage operation. | 2 | Apply 48 VDC to applicable DI threshold variant and toggle 100 times. | 48 | VDC | Correct ON/OFF state |  | N/A | N/A |  |  | Correct state is reported for every operation; no missed/extra transitions.
DI-03 | Representative field-voltage operation. | 3 | Apply 60 VDC to applicable DI threshold variant and toggle 100 times. | 60 | VDC | Correct ON/OFF state |  | N/A | N/A |  |  | Correct state is reported for every operation; no missed/extra transitions.
DI-03 | Representative field-voltage operation. | 4 | Apply 80 VDC to applicable DI threshold variant and toggle 100 times. | 80 | VDC | Correct ON/OFF state |  | N/A | N/A |  |  | Correct state is reported for every operation; no missed/extra transitions.
DI-03 | Representative field-voltage operation. | 5 | Apply 110 VDC to applicable DI threshold variant and toggle 100 times. | 110 | VDC | Correct ON/OFF state |  | N/A | N/A |  |  | Correct state is reported for every operation; no missed/extra transitions.
DI-03 | Representative field-voltage operation. | 6 | Apply 125 VDC to applicable DI threshold variant and toggle 100 times. | 125 | VDC | Correct ON/OFF state |  | N/A | N/A |  |  | Correct state is reported for every operation; no missed/extra transitions.
DI-01 | Low-threshold variant pickup/dropout characterization. | 1 | Ramp upward through nominal 15 V threshold at specified rate. | 15 | V nominal threshold | Record pickup | V | TBD | TBD |  |  | Exact pickup/dropout tolerance is not defined in the specification; characterize and record.
DI-01 | Low-threshold variant pickup/dropout characterization. | 2 | Ramp downward through nominal 15 V threshold and record dropout. | 15 | V nominal threshold | Record dropout | V | TBD | TBD |  |  | Exact pickup/dropout tolerance is not defined in the specification; characterize and record.
DI-02 | High-threshold variant pickup/dropout characterization. | 1 | Ramp upward through nominal 45 V threshold at specified rate. | 45 | V nominal threshold | Record pickup | V | TBD | TBD |  |  | Exact pickup/dropout tolerance is not defined in the specification; characterize and record.
DI-02 | High-threshold variant pickup/dropout characterization. | 2 | Ramp downward through nominal 45 V threshold and record dropout. | 45 | V nominal threshold | Record dropout | V | TBD | TBD |  |  | Exact pickup/dropout tolerance is not defined in the specification; characterize and record.
DAQ-01 | Verify 50 kHz sample rate. | 1 | Capture known periodic waveform and calculate sample interval from exported raw data. | 50 | kHz | 20 | us/sample | TBD | TBD |  |  | Specification defines 50 kHz; allowable sample-clock tolerance is not numerically stated.
TIM-01 | Trip 1 nominal timing. | 1 | Program command-to-confirmation delay of 20 ms using synchronized DI sequence. | 20 | ms | 20 | ms | 19.9 | 20.1 |  |  | Trip 1 time error <= +/-0.1 ms relative to reference sequence.
TIM-01 | Trip 1 nominal timing. | 2 | Program command-to-confirmation delay of 40 ms using synchronized DI sequence. | 40 | ms | 40 | ms | 39.9 | 40.1 |  |  | Trip 1 time error <= +/-0.1 ms relative to reference sequence.
TIM-01 | Trip 1 nominal timing. | 3 | Program command-to-confirmation delay of 60 ms using synchronized DI sequence. | 60 | ms | 60 | ms | 59.9 | 60.1 |  |  | Trip 1 time error <= +/-0.1 ms relative to reference sequence.
TIM-01 | Trip 1 nominal timing. | 4 | Program command-to-confirmation delay of 100 ms using synchronized DI sequence. | 100 | ms | 100 | ms | 99.9 | 100.1 |  |  | Trip 1 time error <= +/-0.1 ms relative to reference sequence.
TIM-05 | Backup trip nominal timing. | 1 | Program command-to-confirmation delay of 20 ms using synchronized DI sequence. | 20 | ms | 20 | ms | 19.9 | 20.1 |  |  | Backup Trip 2 time error <= +/-0.1 ms and event is classified as backup trip.
TIM-05 | Backup trip nominal timing. | 2 | Program command-to-confirmation delay of 40 ms using synchronized DI sequence. | 40 | ms | 40 | ms | 39.9 | 40.1 |  |  | Backup Trip 2 time error <= +/-0.1 ms and event is classified as backup trip.
TIM-05 | Backup trip nominal timing. | 3 | Program command-to-confirmation delay of 60 ms using synchronized DI sequence. | 60 | ms | 60 | ms | 59.9 | 60.1 |  |  | Backup Trip 2 time error <= +/-0.1 ms and event is classified as backup trip.
TIM-05 | Backup trip nominal timing. | 4 | Program command-to-confirmation delay of 100 ms using synchronized DI sequence. | 100 | ms | 100 | ms | 99.9 | 100.1 |  |  | Backup Trip 2 time error <= +/-0.1 ms and event is classified as backup trip.
TIM-08 | Close nominal timing. | 1 | Program command-to-confirmation delay of 20 ms using synchronized DI sequence. | 20 | ms | 20 | ms | 19.9 | 20.1 |  |  | Close time error <= +/-0.1 ms relative to the source signals defined by the specification.
TIM-08 | Close nominal timing. | 2 | Program command-to-confirmation delay of 40 ms using synchronized DI sequence. | 40 | ms | 40 | ms | 39.9 | 40.1 |  |  | Close time error <= +/-0.1 ms relative to the source signals defined by the specification.
TIM-08 | Close nominal timing. | 3 | Program command-to-confirmation delay of 60 ms using synchronized DI sequence. | 60 | ms | 60 | ms | 59.9 | 60.1 |  |  | Close time error <= +/-0.1 ms relative to the source signals defined by the specification.
TIM-08 | Close nominal timing. | 4 | Program command-to-confirmation delay of 100 ms using synchronized DI sequence. | 100 | ms | 100 | ms | 99.9 | 100.1 |  |  | Close time error <= +/-0.1 ms relative to the source signals defined by the specification.
MTR-01 | Motor instantaneous current accuracy. | 1 | Replay normal motor waveform scaled to 0% of 100 A FS. | 0 | % FS equivalent | 0 | A | -1 | 1 |  |  | Instantaneous current within +/-1% FS.
MTR-01 | Motor instantaneous current accuracy. | 2 | Replay normal motor waveform scaled to 25% of 100 A FS. | 25 | % FS equivalent | 25 | A | 24 | 26 |  |  | Instantaneous current within +/-1% FS.
MTR-01 | Motor instantaneous current accuracy. | 3 | Replay normal motor waveform scaled to 50% of 100 A FS. | 50 | % FS equivalent | 50 | A | 49 | 51 |  |  | Instantaneous current within +/-1% FS.
MTR-01 | Motor instantaneous current accuracy. | 4 | Replay normal motor waveform scaled to 75% of 100 A FS. | 75 | % FS equivalent | 75 | A | 74 | 76 |  |  | Instantaneous current within +/-1% FS.
MTR-01 | Motor instantaneous current accuracy. | 5 | Replay normal motor waveform scaled to 100% of 100 A FS. | 100 | % FS equivalent | 100 | A | 99 | 101 |  |  | Instantaneous current within +/-1% FS.
MTR-02 | Motor RMS current accuracy. | 1 | Replay motor-like waveform with independently verified RMS of 10 A. | 10 | A RMS equivalent | 10 | A RMS | 9.5 | 10.5 |  |  | Within +/-0.5% FS as stated in parameter table; note physical channel is specified +/-1% FS and log this discrepancy for clarification.
MTR-02 | Motor RMS current accuracy. | 2 | Replay motor-like waveform with independently verified RMS of 25 A. | 25 | A RMS equivalent | 25 | A RMS | 24.5 | 25.5 |  |  | Within +/-0.5% FS as stated in parameter table; note physical channel is specified +/-1% FS and log this discrepancy for clarification.
MTR-02 | Motor RMS current accuracy. | 3 | Replay motor-like waveform with independently verified RMS of 50 A. | 50 | A RMS equivalent | 50 | A RMS | 49.5 | 50.5 |  |  | Within +/-0.5% FS as stated in parameter table; note physical channel is specified +/-1% FS and log this discrepancy for clarification.
MTR-02 | Motor RMS current accuracy. | 4 | Replay motor-like waveform with independently verified RMS of 75 A. | 75 | A RMS equivalent | 75 | A RMS | 74.5 | 75.5 |  |  | Within +/-0.5% FS as stated in parameter table; note physical channel is specified +/-1% FS and log this discrepancy for clarification.
MTR-02 | Motor RMS current accuracy. | 5 | Replay motor-like waveform with independently verified RMS of 100 A. | 100 | A RMS equivalent | 100 | A RMS | 99.5 | 100.5 |  |  | Within +/-0.5% FS as stated in parameter table; note physical channel is specified +/-1% FS and log this discrepancy for clarification.
MTR-03 | Motor peak current. | 1 | Replay motor-start waveform with known 25 A peak. | 25 | A peak equivalent | 25 | A peak | 24 | 26 | 24.99 | PASS | Peak within +/-1% FS.
MTR-03 | Motor peak current. | 2 | Replay motor-start waveform with known 50 A peak. | 50 | A peak equivalent | 50 | A peak | 49 | 51 | 49.99 | PASS | Peak within +/-1% FS.
MTR-03 | Motor peak current. | 3 | Replay motor-start waveform with known 75 A peak. | 75 | A peak equivalent | 75 | A peak | 74 | 76 | 74.99 | PASS | Peak within +/-1% FS.
MTR-03 | Motor peak current. | 4 | Replay motor-start waveform with known 100 A peak. | 100 | A peak equivalent | 100 | A peak | 99 | 101 | 99.99 | PASS | Peak within +/-1% FS.
MTR-04 | Motor inrush current. | 1 | Replay fast inrush waveform with known 25 A peak. | 25 | A peak equivalent | 25 | A inrush | 23 | 27 |  |  | Inrush value within +/-2% FS and transient is fully captured.
MTR-04 | Motor inrush current. | 2 | Replay fast inrush waveform with known 50 A peak. | 50 | A peak equivalent | 50 | A inrush | 48 | 52 |  |  | Inrush value within +/-2% FS and transient is fully captured.
MTR-04 | Motor inrush current. | 3 | Replay fast inrush waveform with known 75 A peak. | 75 | A peak equivalent | 75 | A inrush | 73 | 77 |  |  | Inrush value within +/-2% FS and transient is fully captured.
MTR-04 | Motor inrush current. | 4 | Replay fast inrush waveform with known 100 A peak. | 100 | A peak equivalent | 100 | A inrush | 98 | 102 |  |  | Inrush value within +/-2% FS and transient is fully captured.
MTR-05 | Motor run time per cycle. | 1 | Generate motor current above run threshold for exactly 1 s. | 1 | s | 1 | s | 0.999 | 1.001 |  |  | Run-time error <= +/-0.1% of measured interval or approved interpretation of timer accuracy.
MTR-05 | Motor run time per cycle. | 2 | Generate motor current above run threshold for exactly 3 s. | 3 | s | 3 | s | 2.997 | 3.003 |  |  | Run-time error <= +/-0.1% of measured interval or approved interpretation of timer accuracy.
MTR-05 | Motor run time per cycle. | 3 | Generate motor current above run threshold for exactly 5 s. | 5 | s | 5 | s | 4.995 | 5.005 |  |  | Run-time error <= +/-0.1% of measured interval or approved interpretation of timer accuracy.
MTR-05 | Motor run time per cycle. | 4 | Generate motor current above run threshold for exactly 10 s. | 10 | s | 10 | s | 9.99 | 10.01 |  |  | Run-time error <= +/-0.1% of measured interval or approved interpretation of timer accuracy.
MTR-05 | Motor run time per cycle. | 5 | Generate motor current above run threshold for exactly 20 s. | 20 | s | 20 | s | 19.98 | 20.02 |  |  | Run-time error <= +/-0.1% of measured interval or approved interpretation of timer accuracy.
LOAD-01 | Load instantaneous current accuracy. | 1 | Inject 333 mV-scaled waveform with known instantaneous current equivalent of 2 A. | 33.3 | mV equivalent | 2 | A Instantaneous | 1.8 | 2.2 | 1.998 | PASS | Instantaneous load-current requirement met within +/-1% FS.
LOAD-01 | Load instantaneous current accuracy. | 2 | Inject 333 mV-scaled waveform with known instantaneous current equivalent of 5 A. | 83.25 | mV equivalent | 5 | A Instantaneous | 4.8 | 5.2 | 4.996 | PASS | Instantaneous load-current requirement met within +/-1% FS.
LOAD-01 | Load instantaneous current accuracy. | 3 | Inject 333 mV-scaled waveform with known instantaneous current equivalent of 10 A. | 166.5 | mV equivalent | 10 | A Instantaneous | 9.8 | 10.2 | 9.994 | PASS | Instantaneous load-current requirement met within +/-1% FS.
LOAD-01 | Load instantaneous current accuracy. | 4 | Inject 333 mV-scaled waveform with known instantaneous current equivalent of 15 A. | 249.75 | mV equivalent | 15 | A Instantaneous | 14.8 | 15.2 | 14.99 | PASS | Instantaneous load-current requirement met within +/-1% FS.
LOAD-01 | Load instantaneous current accuracy. | 5 | Inject 333 mV-scaled waveform with known instantaneous current equivalent of 20 A. | 333 | mV equivalent | 20 | A Instantaneous | 19.8 | 20.2 | 19.99 | PASS | Instantaneous load-current requirement met within +/-1% FS.
LOAD-02 | Load RMS accuracy. | 1 | Inject 333 mV-scaled waveform with known rms current equivalent of 2 A. | 33.3 | mV equivalent | 2 | A RMS | 1.8 | 2.2 |  |  | Reported RMS within +/-1% FS.
LOAD-02 | Load RMS accuracy. | 2 | Inject 333 mV-scaled waveform with known rms current equivalent of 5 A. | 83.25 | mV equivalent | 5 | A RMS | 4.8 | 5.2 |  |  | Reported RMS within +/-1% FS.
LOAD-02 | Load RMS accuracy. | 3 | Inject 333 mV-scaled waveform with known rms current equivalent of 10 A. | 166.5 | mV equivalent | 10 | A RMS | 9.8 | 10.2 |  |  | Reported RMS within +/-1% FS.
LOAD-02 | Load RMS accuracy. | 4 | Inject 333 mV-scaled waveform with known rms current equivalent of 15 A. | 249.75 | mV equivalent | 15 | A RMS | 14.8 | 15.2 |  |  | Reported RMS within +/-1% FS.
LOAD-02 | Load RMS accuracy. | 5 | Inject 333 mV-scaled waveform with known rms current equivalent of 20 A. | 333 | mV equivalent | 20 | A RMS | 19.8 | 20.2 |  |  | Reported RMS within +/-1% FS.
LOAD-03 | Load peak accuracy. | 1 | Inject 333 mV-scaled waveform with known peak current equivalent of 2 A. | 33.3 | mV equivalent | 2 | A Peak | 1.6 | 2.4 |  |  | Peak within +/-2% FS.
LOAD-03 | Load peak accuracy. | 2 | Inject 333 mV-scaled waveform with known peak current equivalent of 5 A. | 83.25 | mV equivalent | 5 | A Peak | 4.6 | 5.4 |  |  | Peak within +/-2% FS.
LOAD-03 | Load peak accuracy. | 3 | Inject 333 mV-scaled waveform with known peak current equivalent of 10 A. | 166.5 | mV equivalent | 10 | A Peak | 9.6 | 10.4 |  |  | Peak within +/-2% FS.
LOAD-03 | Load peak accuracy. | 4 | Inject 333 mV-scaled waveform with known peak current equivalent of 15 A. | 249.75 | mV equivalent | 15 | A Peak | 14.6 | 15.4 |  |  | Peak within +/-2% FS.
LOAD-03 | Load peak accuracy. | 5 | Inject 333 mV-scaled waveform with known peak current equivalent of 20 A. | 333 | mV equivalent | 20 | A Peak | 19.6 | 20.4 |  |  | Peak within +/-2% FS.
FAULT-01 | Fault-current instantaneous accuracy. | 1 | Replay fault waveform with known instantaneous current equivalent of 5 A. | 83.25 | mV equivalent | 5 | A Instantaneous | 4.4 | 5.6 |  |  | Fault instantaneous value within +/-3% FS.
FAULT-01 | Fault-current instantaneous accuracy. | 2 | Replay fault waveform with known instantaneous current equivalent of 10 A. | 166.5 | mV equivalent | 10 | A Instantaneous | 9.4 | 10.6 |  |  | Fault instantaneous value within +/-3% FS.
FAULT-01 | Fault-current instantaneous accuracy. | 3 | Replay fault waveform with known instantaneous current equivalent of 15 A. | 249.75 | mV equivalent | 15 | A Instantaneous | 14.4 | 15.6 |  |  | Fault instantaneous value within +/-3% FS.
FAULT-01 | Fault-current instantaneous accuracy. | 4 | Replay fault waveform with known instantaneous current equivalent of 20 A. | 333 | mV equivalent | 20 | A Instantaneous | 19.4 | 20.6 |  |  | Fault instantaneous value within +/-3% FS.
FAULT-02 | Fault-current peak accuracy. | 1 | Replay fault waveform with known peak current equivalent of 5 A. | 83.25 | mV equivalent | 5 | A Peak | 4 | 6 |  |  | Peak within +/-5% FS.
FAULT-02 | Fault-current peak accuracy. | 2 | Replay fault waveform with known peak current equivalent of 10 A. | 166.5 | mV equivalent | 10 | A Peak | 9 | 11 |  |  | Peak within +/-5% FS.
FAULT-02 | Fault-current peak accuracy. | 3 | Replay fault waveform with known peak current equivalent of 15 A. | 249.75 | mV equivalent | 15 | A Peak | 14 | 16 |  |  | Peak within +/-5% FS.
FAULT-02 | Fault-current peak accuracy. | 4 | Replay fault waveform with known peak current equivalent of 20 A. | 333 | mV equivalent | 20 | A Peak | 19 | 21 |  |  | Peak within +/-5% FS.
ARC-01 | Known arcing interval. | 1 | Generate contact-parting reference and final current extinction separated by 2 ms. | 2 | ms | 2 | ms | 1.9 | 2.1 |  |  | Reported arcing-time error <= +/-0.1 ms.
ARC-01 | Known arcing interval. | 2 | Generate contact-parting reference and final current extinction separated by 5 ms. | 5 | ms | 5 | ms | 4.9 | 5.1 |  |  | Reported arcing-time error <= +/-0.1 ms.
ARC-01 | Known arcing interval. | 3 | Generate contact-parting reference and final current extinction separated by 10 ms. | 10 | ms | 10 | ms | 9.9 | 10.1 |  |  | Reported arcing-time error <= +/-0.1 ms.
ARC-01 | Known arcing interval. | 4 | Generate contact-parting reference and final current extinction separated by 15 ms. | 15 | ms | 15 | ms | 14.9 | 15.1 |  |  | Reported arcing-time error <= +/-0.1 ms.
EVT-01 | Verify pre/post-trigger record length for 200/300 ms events. | 1 | Generate event with identifiable markers and verify pre-trigger window. | 200 | ms | 200 | ms | 200 | 200 |  |  | One continuous record with 200 ms pre-trigger + 300 ms post-trigger; trigger boundary is correct within timing requirement.
EVT-01 | Verify pre/post-trigger record length for 200/300 ms events. | 2 | Generate event with identifiable markers and verify post-trigger window. | 300 | ms | 300 | ms | 300 | 300 |  |  | One continuous record with 200 ms pre-trigger + 300 ms post-trigger; trigger boundary is correct within timing requirement.
EVT-02 | Verify motor 5000/5000 ms capture. | 1 | Generate event with identifiable markers and verify pre-trigger window. | 5000 | ms | 5000 | ms | 5000 | 5000 |  |  | Required 5 s pre-trigger and 5 s post-trigger data are retained without gaps.
EVT-02 | Verify motor 5000/5000 ms capture. | 2 | Generate event with identifiable markers and verify post-trigger window. | 5000 | ms | 5000 | ms | 5000 | 5000 |  |  | Required 5 s pre-trigger and 5 s post-trigger data are retained without gaps.
EVT-03 | Verify short 10/20 ms fault/arcing record. | 1 | Generate event with identifiable markers and verify pre-trigger window. | 10 | ms | 10 | ms | 10 | 10 |  |  | 10 ms pre + 20 ms post capture with correct sequence and no missing samples.
EVT-03 | Verify short 10/20 ms fault/arcing record. | 2 | Generate event with identifiable markers and verify post-trigger window. | 20 | ms | 20 | ms | 20 | 20 |  |  | 10 ms pre + 20 ms post capture with correct sequence and no missing samples.
CNT-01 | Total trip operation count. | 1 | Generate 100 main-trip + 20 backup-trip valid operations. | 120 | operations | 120 | count | 120 | 120 |  |  | Trip operation count matches approved counting rule exactly; bounce does not create extra count.
CNT-02 | Total close operation count. | 1 | Generate 120 valid close operations; failed closes are separate negative checks. | 120 | operations | 120 | count | 120 | 120 |  |  | Valid close count equals expected value; failed operations are counted/not counted according to documented rule.
CNT-03 | Cumulative operation persistence. | 1 | Generate 200 mixed valid operations and verify persistence through resets/power cycles. | 200 | operations | 200 | count | 200 | 200 |  |  | Counters persist without loss or unexplained increment.
STO-02 | 100-event capacity. | 1 | Generate exactly 100 uniquely identifiable events. | 100 | events | 100 | stored events | 100 | 100 |  |  | All 100 expected records are retained in correct chronological order.
STO-03 | Oldest-overwrite behavior. | 1 | Generate 110 events total and verify circular storage retains newest 100. | 110 | events | 100 | stored events | 100 | 100 |  |  | Oldest records are overwritten according to the specified circular policy; newest 100 remain and no index corruption occurs.
INS-01 | Verify model, serial/asset ID, hardware revision, PCB revision, firmware, bootloader and configuration baseline. | 1 | Record all identifiers before power-up. Export or archive the factory/default configuration. Photograph the unit and connectors. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | All identifiers are readable and consistent with the test request. Configuration backup is stored with the test record.
INS-02 | Visual workmanship and connector inspection. | 1 | Inspect enclosure, PCB-visible areas, terminal blocks, LEDs, reset access, labels, SD-card installation and signs of damage or contamination. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No damaged, loose, contaminated or incorrectly fitted parts. Connector labels match documentation.
INS-03 | DIN-rail mounting and approximate mechanical envelope. | 1 | Mount/remove the unit on the intended DIN rail three times. Measure overall D/H/W and verify cable/terminal access. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Secure fit without unintended release. No interference with terminals. Dimensions are consistent with the current mechanical drawing or recorded as a controlled deviation.
INS-04 | Protective earth provision and low-resistance continuity check. | 1 | Verify dedicated PE point. Using a low-current ohmmeter, measure continuity from PE point to accessible chassis metal. This is an engineering continuity check, not a formal safety test. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | A stable low-resistance connection is present; value is recorded. Any intermittent/open connection is a failure.
INS-05 | Establish baseline functional health. | 1 | Apply nominal 24 VDC, allow boot to complete, verify LEDs, local access, Ethernet link, SD-card detection and live readings at zero input. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Device boots without error; no unexpected alarm; all interfaces intended for this build are accessible.
PWR-04 | Brownout characterization below specified range. | 1 | Decrease supply in 0.5 V steps from 21.6 V until the DUT resets or shuts down. Repeat with a slow ramp and a 100 ms step. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Behavior is controlled: no corrupted configuration/counters/event files. Brownout threshold and recovery behavior are documented as characterization.
PWR-05 | Short and repeated interruptions. | 1 | At nominal operation, interrupt supply for 10 ms, 50 ms, 100 ms, 500 ms, 2 s and 10 s. Repeat during idle, event capture, SD write and MQTT publish. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | If the DUT remains powered, acquisition continues correctly. If it resets, it returns to a valid state. No corrupted persistent data or false operation count.
PWR-06 | Reverse-polarity protection. | 1 | With current limit set to a safe value, connect -24 VDC for 10 s. Remove, restore correct polarity and boot. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No damage, excessive current or smoke/odor. DUT functions normally after correct polarity is restored.
PWR-07 | Input fuse / input protection behavior. | 1 | Verify presence/rating of the intended input fuse by inspection and controlled low-voltage overcurrent method approved by hardware engineering. Do not perform destructive certification fault-current testing. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Protection component matches design intent; no unsafe bypass or incorrect assembly.
PWR-08 | Power cycling endurance. | 1 | Automate 500 power cycles: 60 s ON / 10 s OFF. Every 25 cycles generate a breaker event before power removal. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | All cycles recover normally; counters/events remain consistent; no progressive boot-time or storage errors.
AI-04 | Analog input under-range, zero and over-range behavior. | 1 | Apply 0 mA/0 mV, slightly below nominal minimum where possible, and 105%, 110% and 120% of normal terminal signal within safe hardware limits. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No damage or latched invalid state. Over-range is clipped/flagged consistently; normal measurement resumes after returning in range.
AI-05 | Open, short and reverse-polarity sensor fault behavior. | 1 | At each relevant analog input disconnect sensor, short terminal pair through approved low impedance, and reverse polarity only if safe for the input design. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No permanent damage. Diagnostics/logging behave as implemented. Normal measurement returns after fault removal. Any unspecified behavior is recorded.
AI-06 | Channel crosstalk at simultaneous full-scale. | 1 | Drive one channel with full-scale dynamic waveform while adjacent channels are held at 25% FS; rotate through all analog channels. Repeat with all channels active. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Non-driven channels remain within their specified accuracy. No false triggers or waveform artifacts attributable to crosstalk.
AI-07 | Noise immunity characterization at terminal level. | 1 | Superimpose controlled low-amplitude broadband or sinusoidal noise on mid-scale analog signals. Increase until measurement visibly degrades; remain within safe terminal limits. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | At agreed engineering noise level, no false event trigger and measurements remain inside specified tolerance. Threshold of degradation is documented.
AI-08 | Sensor scaling and configuration retention. | 1 | Program each channel scaling, power cycle, hard reset and perform 100 events. Verify scaling remains unchanged unless intentionally modified. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Configured scaling persists and is applied consistently to live data, event files and MQTT outputs.
AV-03 | Voltage sag, interruption and ripple. | 1 | From nominal control voltage, apply 10%, 20%, 40% sag, 100 ms interruption and superimposed ripple. Generate a trip/close event during each condition. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Event capture remains valid; measured voltage reflects the disturbance; no false status or reset.
AV-04 | Over-range and recovery. | 1 | Increase input above 150 V only to the approved engineering over-range limit. Return to normal input. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No permanent damage. Over-range is handled predictably and normal accuracy returns afterward.
AV-05 | 230 VAC desired capability - conditional. | 1 | Execute only if hardware engineering confirms this prototype is designed for 230 VAC. Apply staged AC levels up to approved maximum. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Pass criterion is the approved design requirement. Otherwise mark Not Applicable / Future Option; do not treat as a prototype failure.
DI-04 | Contact bounce rejection / event handling. | 1 | Generate 1-10 ms bounce trains around intended state transition with 0.5-2 ms pulse spacing. Repeat for Trip, Backup Trip, Close, 52A and 52B. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Raw status captures transitions as designed, while event counters/timing do not double-count a single physical operation. Any debounce rule is documented.
DI-05 | Slow edge and threshold dwell. | 1 | Ramp slowly through threshold and dwell within +/-2 V around the switching point for 5 s. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No uncontrolled oscillation or repeated false operation count. Hysteresis behavior is stable.
DI-06 | Short noise pulses. | 1 | Apply sub-threshold and above-threshold pulses of 50 us, 100 us, 500 us, 1 ms and 5 ms. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Behavior is consistent with the sampling/debounce design; no false operation count. Minimum accepted pulse width is characterized.
DI-07 | Simultaneous digital transitions and inter-channel skew. | 1 | Switch all five DIs simultaneously from a common reference trigger. Measure recorded transition timestamps. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Inter-channel timing skew is consistent with +/-0.1 ms system timing requirement or a tighter approved internal target.
DI-08 | Contradictory 52A/52B states. | 1 | Apply both OFF, both ON, delayed complement, overlap and gap states. Repeat during trip and close sequences. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No crash or incorrect counter increment. Contradictory state is logged/flagged if implemented; event record preserves raw DI states.
DAQ-02 | Verify simultaneous sampling / channel alignment. | 1 | Feed the same edge or sine waveform to multiple analog channels through appropriate scaling interfaces. Compare sample index and phase of the captured transition. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No material sequential-scan skew; measured inter-channel skew supports required timing accuracy.
DAQ-03 | Frequency response from DC/low frequency to 20 kHz. | 1 | Sweep low-level sinusoidal input through representative frequencies: 10 Hz, 50 Hz, 100 Hz, 1 kHz, 5 kHz, 10 kHz, 15 kHz, 20 kHz. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Gain/phase response is documented. The product meets the design-defined 20 kHz bandwidth interpretation; if tolerance is not specified, log as open requirement.
DAQ-04 | Anti-alias characterization above 20 kHz. | 1 | Inject frequencies above 20 kHz up to the safe generator/interface limit and observe captured aliased content. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Attenuation trend demonstrates anti-alias filtering. Numeric stop-band criterion is documented as characterization unless defined by design.
DAQ-05 | Noise floor and effective resolution. | 1 | Short/zero the input using the approved termination and capture 10 s of data at room temperature. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Noise floor is stable and does not cause false event detection. RMS noise and peak-to-peak noise are recorded as baseline.
DAQ-06 | Missing/duplicate sample check under maximum activity. | 1 | Run all analog channels with dynamic waveforms, toggle all DIs, publish MQTT and create event files continuously for 30 min. Analyze sample indexes/timestamps. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No unexplained missing/duplicated samples or corrupt waveform segments.
DAQ-07 | Clipping and recovery. | 1 | Drive each analog channel to full scale, then controlled over-range, then back to 50% FS. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Clipping is deterministic; no prolonged recovery artifact; subsequent measurements return to tolerance.
EVT-04 | Back-to-back events. | 1 | Generate two trip/close sequences separated by 1 s, 500 ms, 200 ms and 50 ms. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | System behavior is deterministic: both events are captured when supported, or documented event-rearm rule is applied without file corruption.
EVT-05 | Event longer than post-trigger window. | 1 | Generate motor or coil waveform that intentionally extends beyond configured post-trigger. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Record truncation behavior is controlled and indicated if applicable; no corruption. Requirement gap is logged if complete physical event is expected but window is insufficient.
EVT-06 | Trigger during startup, network load and storage activity. | 1 | Generate events immediately after boot, during MQTT reconnect, during event export and during SD-card rollover. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No crash or corrupted event. Unsupported startup dead time is characterized and documented.
COIL-01 | TC1 normal operation waveform. | 1 | Replay a reference 4-20 mA waveform representing trip-coil pickup, armature movement dip and steady current. Compare instantaneous waveform, RMS and peak to reference. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | TC1 instantaneous and RMS within +/-0.5% FS; peak within +/-1% FS; waveform shape and event timing preserved.
COIL-02 | TC2 normal backup-trip waveform. | 1 | Repeat COIL-01 on TC2 using independent backup-trip command. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | TC2 measurements meet applicable accuracy and event is uniquely identified from TC1.
COIL-03 | Close coil normal waveform. | 1 | Replay normal close-coil waveform with CloseInitiate_Cmd and 52A transition. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | CC instantaneous/RMS/peak accuracy meets specification; close event associated with correct command.
COIL-04 | RMS algorithm verification. | 1 | Apply DC level, sine wave, rectified waveform and realistic coil transient with independently calculated RMS over the firmware-defined window. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Reported RMS agrees with reference within stated accuracy. If RMS window is undocumented, log exact observed/assumed window.
COIL-05 | Peak algorithm verification. | 1 | Replay waveforms with single peak, repeated peaks and narrow spike. Compare reported peak with reference sample-domain maximum. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Reported peak meets specified accuracy and uses a repeatable definition.
COIL-06 | Degraded/faulty coil signatures. | 1 | Replay weak current, excessive current, missing armature dip, open coil, intermittent current, chatter and clipped sensor output. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Raw waveform is captured without corruption; calculated values reflect injected condition; any implemented diagnostic is correctly flagged with no false counter increments.
TIM-02 | Trip 1 fast/slow boundary operation. | 1 | Program very fast and very slow realistic timing while remaining inside event window. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Correct timing is reported without overflow or negative time.
TIM-03 | Trip command without TC1 current. | 1 | Assert TripInitiate_Cmd but keep TC1 at zero; optionally transition 52A. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No fabricated normal coil waveform. Event/raw data show missing current; timing behavior is documented and diagnostic generated if supported.
TIM-04 | TC1 current without trip command. | 1 | Inject TC1 waveform without TripInitiate_Cmd and optionally change 52A. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No false commanded trip count; raw event behavior is consistent with trigger configuration.
TIM-06 | Main trip fails, backup trip succeeds. | 1 | Assert main trip command with no 52A change, then delayed backup trip with TC2 and 52A transition. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Sequence is preserved; backup-trip timing is correct; counters do not double-count the same physical opening.
TIM-07 | Main and backup trip overlap. | 1 | Assert Trip 1 and Backup Trip commands within 0, 1, 5 and 20 ms of each other; drive TC1/TC2 accordingly. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Both source signals are captured; operation counter logic follows approved rule; no corrupted timing.
TIM-09 | Failed close / already closed. | 1 | Issue close command with no 52A transition; repeat when 52A is already ON. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No false successful close count unless approved counter rule says otherwise; event record shows the actual states.
TIM-10 | Bounce and contradictory 52A/52B during timing. | 1 | Add bounce, overlap and missing transitions to otherwise normal trip/close sequence. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No double-counting. Timing result is stable or invalidated/flagged according to algorithm; raw transitions remain available.
MTR-06 | Abnormal motor behavior. | 1 | Replay stalled motor, repeated restart, excessive inrush, low current, interrupted cycle, chatter and motor current with no breaker operation. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Waveforms/cycle data reflect injected condition; no false breaker operation count; implemented diagnostics are correct.
CNT-04 | Counter rollover/reset behavior. | 1 | Use engineering service method or accelerated test mechanism to approach configured counter limit; test authorized reset if available. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No wrap to incorrect negative/zero value unless explicitly designed. Reset requires approved access and is logged if implemented.
LOAD-04 | 50/60 Hz and step response. | 1 | Switch between 50 and 60 Hz, then apply sudden load steps from 10% to 90% FS. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No erroneous fault event solely from frequency change; load value settles predictably.
LOAD-05 | CT/sensor abnormal conditions. | 1 | Open the 333 mV sensor output, short the input as allowed, reverse polarity, apply low-amplitude noise and scaling mismatch. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No damage; readings and diagnostics behave predictably; normal operation returns after fault removal.
FAULT-03 | Fault inception angle and DC offset. | 1 | Replay 50/60 Hz faults starting at 0, 30, 60 and 90 electrical degrees with several DC offsets. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Event is captured without sample loss; calculated instantaneous/peak remain within applicable tolerance.
FAULT-04 | Fault threshold boundary characterization. | 1 | Sweep current around the firmware fault-classification threshold. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Threshold and hysteresis are repeatable. If threshold is not specified, log it as an open requirement rather than creating a hidden acceptance limit.
ARC-02 | Multiple current zero crossings before final extinction. | 1 | Replay AC fault current that crosses zero naturally several times before final current extinction. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Algorithm uses final extinction according to approved definition; result matches reference within +/-0.1 ms.
ARC-03 | Low current, current chopping and DC offset. | 1 | Replay low-amplitude interruption, chopped current and offset waveforms. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Arcing time remains stable when above detection capability; any minimum current criterion is documented.
ARC-04 | Incorrect/missing 52A reference. | 1 | Shift 52A early/late and then remove the 52A transition. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Calculated result changes consistently with source reference or is invalidated; no silent presentation of a misleading valid arcing time.
WEAR-01 | Single-event I^2t calculation. | 1 | Replay a known current waveform. Independently integrate I^2 over the algorithm-defined arcing interval using reference samples. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | DUT event wear result agrees within +/-0.5% if this requirement applies to algorithm output; otherwise deviation/open requirement is recorded.
WEAR-02 | Cumulative wear across multiple events. | 1 | Replay a sequence of at least 50 interruptions with different current magnitudes and durations. Maintain independent cumulative I^2t. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | DUT cumulative value tracks reference without missed/duplicate event contribution and persists through power cycles.
WEAR-03 | Boundary/fault behavior. | 1 | Replay zero-current operation, clipped current, missing Ia, invalid arcing reference and over-range waveform. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Invalid data are not silently accumulated as valid wear. Device behavior is logged and any quality flag requirement is raised if absent.
RST-01 | No-restrike baseline and single restrike. | 1 | Replay one interruption with clean final extinction and one with a programmed post-extinction current reappearance. Repeat at several amplitudes/times. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No-restrike case produces no flag; valid injected restrike produces the event flag according to algorithm settings.
RST-02 | Multiple restrikes / re-ignitions. | 1 | Replay two or more separated post-zero current bursts within the capture window. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Restrike event is flagged and raw waveform retains all injected bursts.
RST-03 | False-positive robustness. | 1 | Replay CT ringing, low-level noise, harmonic distortion, narrow switching spikes and residual current without true restrike. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No false flag at the approved engineering waveform set. Detection threshold and minimum duration are logged if not already specified.
STO-01 | Create, view/export and verify event files. | 1 | Generate 10 events of different types. Export each and correlate ID, timestamp, waveform, parameter values and source command. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | All events are present, readable and correctly associated with the injected sequence.
STO-04 | Power loss during SD write. | 1 | At least 50 times, remove DUT power at randomized delay 0-500 ms after event completion/record start. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | After reboot, file system remains usable; prior completed events/counters are intact; partially written event is handled deterministically and logged if applicable.
STO-05 | Missing/removed/corrupt SD-card behavior. | 1 | Boot without card, remove card when idle, simulate full/slow/corrupt media using engineering tools as safe. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Device does not crash; storage fault is indicated/logged; real-time acquisition either continues or fails in a controlled documented manner.
STO-06 | Deletion and retention. | 1 | Delete selected events through supported interface, reboot, and verify remaining records. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Only selected records are removed; configuration and counters remain intact. No deleted record reappears.
COM-01 | Ethernet 10/100 link and reconnect. | 1 | Connect through 10 Mbps and 100 Mbps capable switch, disconnect cable for 1 s/10 s/5 min and reconnect. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Link recovers without reboot; acquisition continues; no event corruption.
COM-02 | MQTT payload correctness. | 1 | Publish live measurements and event data to test broker. Capture packets and compare values/timestamps to DUT event files. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Published points match internal values and channel mapping. Topic/payload structure matches current functional definition.
COM-03 | Broker unavailable and restart. | 1 | Stop broker for 1, 10 and 60 min while generating events; restart broker. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | DUT remains responsive, no acquisition loss. Reconnect behavior is deterministic; any buffering/store-forward behavior is documented.
COM-04 | Network congestion / high traffic. | 1 | Generate sustained broadcast/unicast traffic on test LAN while triggering rapid events and exporting records. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No missing samples, event loss or watchdog reset attributable to network load.
COM-05 | Repeated connect/disconnect endurance. | 1 | Perform 500 Ethernet or broker reconnect cycles during a 4 h automated event run. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No progressive resource leak, hang or loss of measurement function.
COM-06 | RS-485 basic functional link. | 1 | Connect supported engineering master; verify communication at all implemented baud/parity settings. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Correct responses and no acquisition interruption. Protocol/register details are recorded from the implemented build.
COM-07 | RS-485 wiring/fault recovery. | 1 | Reverse A/B, open line, add/remove termination and reconnect master. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No damage or reboot. Link recovers after correct wiring is restored.
UI-01 | Power LED indication. | 1 | Cycle power and observe LED at off, boot and normal operation. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Green when power/defined normal state is present; OFF when unpowered, consistent with specification.
UI-02 | Status LED normal/error indication. | 1 | Observe normal state, then inject supported storage/communication/sensor error conditions. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Green normal; Red error when a qualifying fault is detected. Exact fault mapping is documented.
UI-03 | Hard reset from idle and active event. | 1 | Press reset during idle, event capture, SD write and MQTT session. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Device reboots to a valid state. No persistent data corruption or unexplained counter change.
UI-04 | I/O access and field-service usability. | 1 | Install/remove field wires using intended terminal hardware; verify labels and tool clearance. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | All I/O can be safely accessed without removing unrelated wiring; no mechanical damage after repeated service cycles.
DIAG-01 | Storage fault diagnostics. | 1 | Remove/misconfigure SD card and generate events. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Fault is detected and error is logged with useful context.
DIAG-02 | Sensor/input fault diagnostics. | 1 | Apply open/short/over-range analog conditions and contradictory DIs. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Implemented diagnostics identify the fault without causing false operation count.
DIAG-03 | Communication fault logging. | 1 | Disconnect Ethernet/RS-485 and stop MQTT broker. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Communication fault/recovery is logged if implemented; acquisition continues.
DIAG-04 | Error-log retention and timestamp. | 1 | Create at least 20 different faults, power cycle and review logs. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Logs remain readable, ordered and time-correlated; no unrelated data corruption.
ENV-01 | Cold functional operation. | 1 | Condition prototype at available chamber steps toward -40 degC. At each stable point run baseline I/O accuracy, event and communications checks. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No functional loss; measured drift remains within product accuracy requirements at the stated operating range. If chamber cannot reach -40 degC, record achieved limit.
ENV-02 | Hot functional operation. | 1 | Condition toward +70 degC and repeat baseline measurement/event/communications checks. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No reset, storage fault or accuracy failure. Internal temperature/thermal observations recorded.
ENV-03 | Temperature cycling engineering stress. | 1 | Perform multiple room-cold-room-hot-room cycles within available chamber capability, with powered operation when safe. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No connector/mechanical issue, calibration shift or data corruption. This is not standard qualification.
ENV-04 | High-humidity functional check where available. | 1 | Expose to a controlled non-condensing high-humidity condition within safe equipment capability; run reduced functional suite. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No condensation, leakage-related malfunction or measurement instability. Formal 5-95% RH qualification remains third-party.
END-01 | 30-day powered stability recommendation. | 1 | Operate continuously with all channels active, MQTT connected and periodic event generation. Daily automated health checks and weekly accuracy spot checks. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No unplanned reset, memory leak symptom, storage corruption or progressive measurement drift beyond requirements.
END-02 | High-cycle event endurance recommendation. | 1 | Automate at least 10,000 mixed trip/close sequences and at least 1,000 motor cycles if schedule permits. Include 100-event storage rollover repeatedly. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Counters match generated sequence, no event-management corruption, no increasing latency or missed triggers.
END-03 | Repeated fault/restrike waveform endurance. | 1 | Replay at least 1,000 fault-current events with varied arcing/restrike patterns over several days. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Fault, arcing, wear and restrike calculations remain consistent; no cumulative algorithm/storage defect.
INT-01 | Low product supply during trip | 1 | Operate DUT at 21.6 VDC, apply low control-voltage condition, then trip event with normal TC1/52A. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Trip event captured; timing/coil values within accuracy; voltage sag visible; no reset.
INT-02 | Main trip fails, backup trip succeeds | 1 | Main command + TC1 without 52A, followed by delayed backup command + TC2 + 52A. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Backup operation identified; timing correct; one physical opening counted according to approved counter logic.
INT-03 | High fault current with restrike | 1 | Trip event with Ia fault waveform, known arcing interval and post-zero restrike. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Fault current, arcing time, wear contribution and restrike flag all match reference.
INT-04 | Power loss during fault-event storage | 1 | Generate fault event and interrupt 24 VDC during SD write. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Previous data intact; reboot valid; partially written event handled deterministically.
INT-05 | Network congestion during breaker event | 1 | Saturate test LAN while generating trip/close and motor event. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No missed samples or event; MQTT may delay but acquisition remains correct.
INT-06 | Contact bounce with noisy coil current | 1 | Add DI bounce and analog noise to nominal trip. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No double-count; timing remains within tolerance or is correctly flagged invalid.
INT-07 | Incorrect CT polarity / scaling | 1 | Reverse Ia polarity and apply wrong scaling configuration, then fault event. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Raw waveform reflects polarity; no crash; configuration error is visible in data and does not corrupt other channels.
INT-08 | Missing 52A during trip | 1 | Trip command + TC1 + Ia but no 52A transition. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No misleading valid timing/arcing result; event captures missing 52A condition.
INT-09 | Contradictory 52A/52B states | 1 | Force both ON during close/trip transitions. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Raw status preserved; no double counter; diagnostic/quality behavior documented.
INT-10 | Rapid open-close-open sequence | 1 | Issue trip, close and trip with minimum practical separation. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Each operation captured according to rearm rules; no merged/corrupt events.
INT-11 | Motor start during storage rollover | 1 | Trigger spring motor while event 101 overwrites oldest record. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Motor event captured; circular storage remains consistent.
INT-12 | Breaker event immediately after boot | 1 | Trigger valid event at 0.5, 1, 2 and 5 s after power-up. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Minimum reliable post-boot capture time characterized; no corrupted event.
INT-13 | Sensor over-range plus network outage | 1 | Over-range motor or coil input while broker is unavailable. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No damage; local event/storage remains operational; communication recovery independent.
INT-14 | Hard reset during active motor run | 1 | Reset DUT mid-way through long motor waveform. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Reboot controlled; counters/storage not corrupted; incomplete event handled deterministically.
INT-15 | Low load followed by fault inception | 1 | Operate at low 50/60 Hz load then inject asymmetrical fault at controlled inception angle. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Transition captured; fault values within tolerance and pre-trigger includes pre-fault load.
INT-16 | Chattering command/status wiring | 1 | Generate repeated short Trip/Close pulses without valid coil current. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No excessive operation counter increments or file flood beyond trigger design; raw data/logging supports diagnosis.
INT-17 | All analog channels active + all DIs toggling | 1 | Drive all channels dynamically with synchronized realistic signals for 30 min. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No crosstalk, missed sample, watchdog reset or file corruption.
INT-18 | Temperature extreme + minimum supply (optional) | 1 | At cold/hot engineering chamber point, operate at 21.6 VDC and generate events. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | No functional loss; measurements remain within requirements.
INT-19 | SD-card unavailable + breaker operations | 1 | Remove/disable SD card, continue generating operations. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Device remains stable; storage fault clear; core acquisition behavior documented; counters handled consistently.
INT-20 | Site correlation with actual breaker (optional) | 1 | Capture at least 10 open and 10 close operations on a safe breaker/test bay using production-intent sensors. | N/A |  | Per test acceptance |  | N/A | N/A |  |  | Lab and site event signatures are qualitatively consistent; calculated timing/current values agree with independent breaker/test equipment within defined tolerances.
Note on D49: Procedure not mentioned properly.
Note on D50: Procedure not mentioned properly.
Note on D51: Procedure not mentioned properly.
Note on E85: Bhavishith K: Input= 58.8672mV
Note on E86: Harshitha Malethodi: Input= 117.7344081mV
Note on E87: Harshitha Malethodi: Input= 176.6016122mV
Note on E88: Harshitha Malethodi: Input: 235.4688163mV
Note on D150: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hard reset not present in scematic
Note on B207: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Power LED not present in schematic
Note on B209: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hard reset not present in schematic